## Selection
Pressure Requirements | Feet | PSI |  | Conservative Demand Table
Static Head | 30 | 12.93 |  | Flow Units | Tanks | Flushometers
System Friction Loss | 3 | 1.6162 |  | 100 | 44 | 68
Desired Outlet Pressure | 138.6 | 60 |  | 200 | 65 | 91
System Pressure Requirement |  | 74.5463 |  | 300 | 85 | 110
Minumum City Pressure | 92.4 | 40 |  | 400 | 105 | 125
Required Boost | 79.8018 | 34.5463 |  | 500 | 125 | 140
PRV loss | 11.55 | 5 |  | 750 | 170 | 175
Total Boost | 91.3518 | 39.5463 |  | 1000 | 210 | 218
|  |  |  | 1250 | 240 | 240
Flow Requirements | Flow Units | Qty | Total | 1500 | 270 | 270
Bath Group FV or FT | 8 | 91 | 728 | 1750 | 300 | 300
Tub | 4 | 0 | 0 | 2000 | 325 | 325
WC Flushometer | 7 | 0 | 0
WC Tank | 5 | 0 | 0 |  | Precise Demand Table
Urinal | 5 | 0 | 0 | Flow Units | Light | Med. | Heavy
Lavatory | 2 | 0 | 0 | 1-600 | 80 | 100 | 130
Kitchen Sink | 2 | 1 | 2 | 600-900 | 100 | 120 | 140
Slop Sink | 3 | 0 | 0 | 900-1200 | 120 | 140 | 160
Washing Machine | 4 | 4 | 16 | 1200-1500 | 140 | 160 | 180
Hose Bibb | 3 | 0 | 0 | 1500-2000 | 160 | 190 | 220
Drinking Fountain | 1 | 0 | 0
Shower | 2 | 0 | 0
Dishwasher | 2 | 0 | 0 | Pick Pressurizer for
Other | 4 |  | 0 | 68 | GPM @ | 39.5463 | PSI Boost
Other | 3 |  | 0 | Pressurizer
Other | 10 |  | 0 | Model | Max GPM | Max Boost
Other |  |  | 0 | PB-50 | 50 GPM | 40 PSI
Total |  | 96 | 746 | PB-60 | 60 GPM | 45 PSI
|  |  |  | PB-75 | 75 GPM | 60 PSI
|  |  |  | PB-100 | 100 GPM | 65 PSI
Note on B3: Enter height of Bldg from water meter to top plumbing fixture
Note on C5: Enter desired outlet pressure for last fixture. Usually 40 with a minimum of 25
Note on C7: Enter minimum city pressure. If unsure enter the minimuum of 5
Note on C13: Enter the number of each fixture type. Typical for this entire column
Note on B26: Enter the quantiies of any other water consuming device in these six columns. I.E. lawn sprinklers, commercial washers etc.
Note on C26: Enter the flow units of the other devices. If gpm is known then 1gpm = 2 flow units
Note on G2: Use this table when there are no restrictions on size horsepower etc.
Note on H16: Use this table if there are restrictions to horsepower, size or price.
Note on H17: Use this column for residences, office or schools
Note on I17: Use this column for hotels or resturants
Note on J17: Use this column for health care facilities
Note on D30: Match this figure in Tables 1 or 2 to determine GPM requirements
Note on G26: Enter the calculated GPM here
Note on A4: Default to 10% of static. If actual friction loss is known, unprotect sheet and enter into cells B3 &C3
Note on A5: 40 PSI is recommended. Minimum is 30 PSI
Note on A7: Water prssure at pressuruizer location. If this inforrmation could not be determined use 5 PSI

## Directions
Beige shaded cells are static text and are locked. To change
contents of these or any other cell, from the Tools menu choose"Protection
and "Unprotect". Locked cells on the price sheet cannot be changed.
Red shaded cell are where the user needs to enter information
Where there is a red triangle in the corner the user can place the cursor over the cell
and information or instructions will be displayed. Move the cursor
off the cell and the diplay will go off the screen
This is typical for any color cell with a red triangle in the upper right corner
Blue shaded cells will contain calculated values based on the information
entered in the red cells
1- Enter the height of the building from the water meter to the highest fixture
2- Enter the desired outlet pressure at the furthest fixture. 30 PSI min 40 PSI recommended
3- Enter the minimum system pressure usually known by Bldg maintenance
4- Enter the quantities of the fixturers in the building and any other water consuming devices
5- Read total flow units at the bottom of the table
6- Using either of the two tables on the right, determine the GPM requirements. The upper
table is used when there are no restriction to physical dimensions, horsepower or price of the booster
The lower table is used when such restrictions are present. For instance if the flow units is 200
from the upper table determine 65 GPM for buildings with tank type toilet and 91 for flushometers
From the lower table select 80 gpm to a maximum of 600 flow uints.
7- Enter the determined GPM in cell E23. The calcualted boost is in the next cell to the right
8- Determine which pressurizer is required form the table below. For instance if the gpm requirement
is determined to be 70 and the boost pressure is calculated to be 50 Select a PB 75
9- Click the Pricing tab in the lower left corner of the screen and the price sheet is displayed
10- Select the Pressurizer based on voltage, phase and ASME requirements.
Note on B6: Brian Howley: